## Slide 1: AI-Based Anomaly Detection for Enhanced Performance in Low-Voltage Distribution Networks
Klemen Nagode, Ph.D. – Project Manager
Bilbao, Spain
18-20 November 2025
Session: AI in Practice – Part 2

## Slide 2
Agenda
–
Company profile
Outline of problem
Development of algorithm for fault identification
Results – practical examples of anomaly detection
Conclusion
Opentunity project – modules providing services

## Slide 3
Elektro Ljubljana d.d.
The largest
electricity distribution
network in Slovenia
–
5 distribution units
Distribution area of Elektro Ljubljana
Ljubljana City DU
Ljubljana Environs DU
Novo mesto DU
Trbovlje DU
Kočevje DU

## Slide 4
Outline of problem
–
Fault localization in highly-branched LV network with a large amount of data
DETERMINING ESSENTIAL DATA SETS
Offline: metering system, planned and unplanned events from SCADA system (control centre)
Real-time: ADMS SCADA data from HV and MV, on LV only load-flow and state-estimation, data from protection relays,…
GOAL: A long-term research effort enabling early fault identification, predictive maintenance, and enhanced network reliability.

## Slide 5
Development of algorithm
–
Supervised machine learning
Classification
PREPARATION/DATA ENGINEERINGII
DETERMINATION OF FEATURES
LEARNING & TEST DATA SEPARATION
MODEL LEARNING
DATA VALIDATION
INFORMING MAINTENANCE TEAMS
-querry/export data
-coarse filtration
-filtration based on Events on power meters
-26 features
-principal component analysis PCA 99 % var (reduction of features 26 → 10 linear comb. of originals + orthogonality)
-90 % DATA → LEARNING (k-fold=3
cross-validation)
-10 % DATA → TEST
-hyperparameter optimization
-Confusion matrix
-ROC curve
-Accuracy: LEARNING & TEST DATA
-multiple different algoritms
5 distribution units
MODEL IMPROVEMENT
ERRORS CONFIRMED/DENIED BY MAINTENANCE TEAMS
ON-SITE
INSPECTION

## Slide 6
Development of algorithm
–
weighted kNN
Euclidean distance metric
Number of neighbours k=10
Inverse-squared distance weight w
Features calculation, normalization & PCA
determined features iteratively evaluated by different criterions:
minimum redundancy maximum relevance (MRMR)
univariate feature ranking (chi-square test)
analysis of variances (ANOVA)
2-step normalization:
robust normalization (median & interquartile range)
min-max scaling (transforms data in specific range)
handling outliers
PCA:
orthogonal linear transformation
eigenvectors of features‘ covariance matrix
weighted kNN (with PCA var=99%)

## Slide 7
Development of algorithm
–
weighted kNN
Euclidean distance metric
Number of neighbours k=10
Inverse-squared distance weight w
CONFUSION MATRIX
learning data
test data

## Slide 8
LV 3-phase line
LV 3-phase line
LV 3-phase line
LV 3-phase line
Kočevje DU
Results
–
weighted kNN
Euclidean distance metric
Number of neighbours k=10
Inverse-squared distance weight w
Practical examples of anomaly detection
FEEDBACK FROM MAINTENANCE GROUP
Bad contact on N line branch terminal,
located on A-wooden pillar
Bad contact
on N line
Bad contact
on N line
Bad contact
on N line
Bad contact on N line
No error
Bad contact
on N line
Bad contact on N line
missing voltage: phase 2 and 3
Novo mesto DU

## Slide 9
modules providing services and technologies for grid operators
1. Methodology to ensure interoperability and integration of TSO/DSO available infrastructure into software platforms
Network Planning and Investment deferral from optimal use of flexibility
2. Upgrading topology identification and state estimation
Low-cost Real-Time thermal rating
Advanced Asset Management
Long-Term & Short-Term

## Slide 10
Conclusion
–
The greatest obstacle: determination which features have highest impact on machine learning performance (classification)
Early involvement of maintenance groups helped us with feedback error verification and further co-creation of AI-based anomaly detection
Advantages of AI-based methodology: setting nonlinear boundaries between classes, fast prediction speed, on-line learning on new data → worthwhile use in detecting faults in the LV network
Currently, development is towards automating the entire AI framework on LV distribution network and integration with other systems
AI-based anomaly detection helps operation and maintenance teams to predictive troubleshooting and enhancing low voltage network reliability